PLEASE NOTE: The following specification contains areas, highlighted in yellow and with the [ ] symbol. In these areas, the engineer must make a selection, add specific, project related information and should delete what is not applicable for the specific project.

PART 1 GENERAL

  - Section includes:

    - A single or dual channel water quality sensor transmitter with a local user interface AND the ability to access sensor data remotely through a browser enabled device.

[ ] Single channel [ ] Dual channel

    - Scope

      - Provide labor, material, equipment, related services, and supervision to install and operate the controller to drawings and manufacturer’s specifications.

    - Alternates

      - Parameter-specific controllers that do not allow changing parameter configurations in the field are unacceptable.

      - Controllers or transmitters without the possibility to access data through an internet browser enabled device and cannot present real-time instrument diagnostics are not acceptable.

  - System Descriptions

    - Design requirements

      - Includes capability to actively monitor all internal components and present diagnostics on the overall health of connected sensors and time to next required maintenance, reducing user risk.

        - Ability to see and be notified of upcoming and past due maintenance.

      - Includes capability to provide real-time alerts when sensor issues occur with built in workflows with step-by-step guidance to perform calibration and maintenance tasks, reducing user risk.

      - Includes ability for a cellular network coverage OR Wi-Fi connection OR a LAN connection.

      - Supports advanced communication protocols, including Profibus DPV1, Modbus TCP/IP, Profinet IO, and Ethernet IP.

      - Provides capability to view all connected plant measurements, alerts, calibration, and maintenance status in real time on any internet browser capable device.

        - Connects with overall data system for real time graphic of both online and laboratory data for a full picture of functional plant operational capability.

      - Controller designed to be used in indoor or outdoor locations.

    - Performance Requirements

      - The controller accepts digital sensors in any combination to measure the following water quality parameters:

        - pH/ORP

        - Conductivity

        - Dissolved Oxygen

        - UV Organics

        - Sludge level

        - Ammonium

        - Ammonia

        - Nitrate

        - Combination Ammonium and Nitrate

        - Total suspended solids

        - Orthophosphate

        - Turbidity

        - Free/total Chlorine

        - Combination Chlorine HOCl /Chlorine+Acid / Total free chlorine

        - Ozone in water

        - Chlorine Dioxide

        - Oil in Water

        - Nitrite

    - Environmental Requirements

      - Operational Criteria

        - Operating Temperature:

          - Ethernet version: –20 to 45 °C (–4 to 113 °F)

Cellular version including Controller and external Cellular USB BOX: -20 to 60

°C (-4 to 140 °F)

          - Wi-Fi version including Controller and external Wi-Fi USB BOX: -20 to 60 °C (- 4 to 140 °F)

        - Storage temperature: –20 to 70 °C (–4 to 158 °F)

        - Relative humidity: 0 to 95%, non-condensing

        - Altitude ≤3000m (6,562 ft.)

  - Certifications

    - EMC: CE approved (with all sensor types). Listed for use in general locations to UL and CSA safety standards by ETL (with all sensor types).

    - Safety: General Purpose UL/CSA 61010-1 with cETLus safety mark

    - Possibility for Hazardous Locations Use: Class 1 Div 2

  - Warranty

    - Warranted for 1 year from date of shipment from manufacturer defects.

  - Unscheduled Maintenance

    - Clean controller face

    - Calibrate mA output signals PART 2 PRODUCTS

  - Manufacturer

    - Hach Company, Loveland, Colorado and Hach Lange GmbH, Berlin, Germany

      - SC4500 Controller

  - Manufactured Unit

    - Microprocessor-based sensor controller.

    - Change digital sensors connected to the controller by unplugging and plugging in sensors as necessary.

    - Modules for connection of Analogue sensors for pH, ORP or Conductivity

    - The controller is available with the following power requirements:

AC powered: 100–240 VAC ±10%, 50/60 Hz; 1 A (28 W sensor load)

DC powered: 24 VDC +15% –20%; 2.5 A (20 W sensor load)

    - The controller uses a menu-driven operation system.

    - The controller is equipped with a real-time clock.

    - The controller is equipped with two security levels.

    - The controller shall have worded operation menus in 24 languages.

    - The controller is equipped with an USB reader for data download and controller software upload.

    - High voltage:

Two relays (SPDT);

Wire gauge: 0.75 to 1.5 mm2 (18 to 16 AWG)

AC controller

Maximum switching voltage: 100–240 VAC

Maximum switching current: 5 A Resistive/1 A Pilot Duty Maximum switching power: 1200 VA Resistive/360 VA Pilot Duty DC controller

Maximum switching voltage: 30 VAC or 42 VDC Maximum switching current: 4 A Resistive/1 A Pilot Duty

Maximum switching power: 125 W Resistive/28 W Pilot Duty

    - Five analogs 0/4-20 mA outputs are provided with a maximum impedance of 500 ohms.

      - The controller can be equipped with five 4-20 mA outputs with a maximum impedance of 500 ohms.

      - The following can be programmed:

        - Alarms:

          - High and Low alarm point

          - High and Low alarm point deadband

          - On and Off delay

        - Controls

          - Linear

          - PID

    - The controller can be equipped with the following forms of communication:

      - Profibus DP

      - Modbus TCP/IP

      - Profinet (ODVA certified)

      - Ethernet IP (ODVA certified)

    - The controller can host one of the compatible RTC modules

    - All user settings of the controller are retained for 10 years in flash memory.

    - The controller is equipped with a system check for:

      - Motherboard temperature

      - Field auto-test

  - Equipment

    - Materials

      - Housing: polycarbonate, aluminum (powder coated), and stainless steel Metal enclosure with a corrosion-resistant finish

      - Rating: UL50E type 4X, IEC/EN 60529–IP 66, NEMA 250 type 4X

    - Conduit openings: 0.5 in. NPT

  - Components

    - To deliver:

      - Controller as described in section 1.1.A

      - Mounting hardware for wall, pipe, and panel mounting

      - User manual and installation documentation

    - Dimensions: Refer to controller drawings

    - Weight: 1.7 kg (3.7 lbs.)

  - Instrument Options & Accessories

************************************************

Must be added to instrument at time of order.

************************************************

[ ] Power cord (specify geography)

[ ] Hazardous location rating (C1D2)

[ ] Internet Connection (via LAN, Cellular, or Wi-Fi)

[ ] Modbus TCP/IP

[ ] 4-20mA input module

[ ] 4-20mA output module, 5 outputs

[ ] Profibus DP network module [ ] Profinet IO (ODVA certified)

[ ] Ethernet IP (ODVA certified)

[ ] M12/RJ45 connector kit (Ethernet cable) [ ] M12/M12 connector kit (Ethernet cable) [ ] LZY472-01 USB adapter

[ ] Ethernet cable M12 to M12, 10 m [ ] Ethernet cable M12 to RJ45, 5 m

[ ] Mobile holder

[ ] Memory-Stick (USB)

[ ] UV protection screen

[ ] UV protection screen with sun roof [ ] Cellular USB Box

[ ] Wi-Fi USB Box

[ ] RTC Module

****************************************************************************

PART 3 EXECUTION

  - Preparation

    - Mounting

      - Mount the controller as shown on the drawings

  - Installation

    - Install controller following transmittal drawings and instrument user manual.

  - Manufacturer’s Service and Start-Up

    - Contractor will include manufacturer’s services to perform commissioning of the system to include device provisioning to communicate via local protocols and initiate initial product configuration

    - Contractor will include the manufacturer’s services to perform start-up on instrument to include basic operational training and certification of performance of the instrument.

    - Contractor will include a manufacturer’s Service Agreement that covers all the manufacturer’s recommended preventative maintenance, regularly scheduled calibration and any necessary repairs beginning from the time of equipment startup through to end user acceptance / plant turnover and the first 12 months of end-user operation post turnover.

    - Items A and B are to be performed by manufacturer’s factory-trained service personnel. Field service and factory repair by personnel not employed by the manufacturer is not allowed.

    - Use of manufacturer’s service parts and reagents is required. Third-party parts and reagents are not approved for use.

END OF SECTION